SCHOOL OF COMPUTING AND ENGINEERING SCIENCES (SCES)

BACHELOR OF SCIENCE IN ELECTRICAL AND ELECTRONICS

ENGINEERING (BSEEE)

CONTROL SYSTEMS 2

Lab 4:

STORAGE TANK LIQUID LEVEL CONTROL USING A PLC

BY

Edward Mwongela

(GROUP 5)

Lecturer: Prof. Jackson Mbuthia

29th October 2024

Table of Contents

List of figures	2

1.	Title:	3

2.	Objective:	3

3.	Learning Outcome:	3

4.	Homework to be done as group work.	4

I.	Introduction	4

II.	Programmable Storage Tank Liquid Level Control Preparations	5

5.	Practical Experiment	9

6.	Lab Report	9

# List of figures

Figure 1. liquid level control	4

Figure 2. Allen-Bradley Micro810 PLC CPU	4

Figure 3. float switch	4

# Title:

Storage Tank Liquid Level Control Using a Programmable Logic Controller

# Objective:

- Use a programmable controller output to control a pump

- Use the tank level on/off switches as inputs to the programmable controller

# Learning Outcome:

- Learn how to implement a simple closed loop Bang-Bang controller using a programmable controller.

- Understand the advantages of using a programmable controller to control a pump.

# Homework to be done as group work.

## Introduction

Fig. 1 shows the tank filling arrangement. The sensors shown are implemented using the float switch shown in Fig.2. The float switches are connected to the input terminals of the Micro810 PLC shown in Fig. 4 and the pump motor supply is connected to the output terminals of the Micro810 PLC.

Figure 1. liquid level control

Figure 2. Allen-Bradley Micro810 PLC CPU

Figure 3. float switch

## Programmable Storage Tank Liquid Level Control Preparations

To learn how to program and upload code into the Micro810 PLC, you can download the latest version of Connected Components Workbench for your Micro800 at the URL below.

http://www.rockwellautomation.com/global/products-technologies/connectedcomponents/

You will need to create a free account to access the documentation.

- Physically Confirm that the name plate ratings of the Micro810 PLC supplied to you allow its direct connection to the 240AC mains and the outputs relay contacts have the adequate current and voltage ratings to drive the pump motor and write down the appropriate ratings.

- Refer to the Micro810 PLC Connected Components Work Bench manuals here to prepare a wiring diagram showing the float switches connected as inputs of the Micro810 PLC and the Pump Motor supply connected to the Micro810 PLC outputs.

- Refer to the Connected Components Work Bench Manuals here to write a program to override float switches and run pump for 2 minutes.

PROGRAM PumpControl

VAR

FloatSwitch1 : BOOL;       // Input for Float Switch 1

FloatSwitch2 : BOOL;       // Input for Float Switch 2

Pump : BOOL;               // Output for Pump

ManualOverride : BOOL;     // Manual Override Input

PumpTimer : TON;           // Timer for 2 minutes

END_VAR

// Set the timer duration to 2 minutes

PumpTimer(IN := FALSE, PT := T#2m);

// Pump Control Logic

IF (NOT FloatSwitch1 AND NOT FloatSwitch2) OR ManualOverride THEN

IF NOT PumpTimer.Q THEN

Pump := TRUE;             // Activate pump

PumpTimer(IN := TRUE);    // Start the timer

END_IF;

ELSE

Pump := FALSE;                // Deactivate pump if float switches indicate full and override is off

PumpTimer(IN := FALSE);       // Reset the timer

END_IF;

// Check Timer Done Status

IF PumpTimer.Q THEN

Pump := FALSE;                // Stop pump when timer is done

PumpTimer(IN := FALSE);       // Reset the timer for future cycles

END_IF;

END_PROGRAM

- Refer to the Connected Components Work Bench Manuals here to write a program to override float switch for Tank A but only run the pump for 2 minutes when Tank B switch is ON.

PROGRAM TankAControl

VAR

FloatSwitchTankA : BOOL; // Input for Float Switch of Tank A

FloatSwitchTankB : BOOL; // Input for Float Switch of Tank B

Pump : BOOL; // Output for Pump

ManualOverrideTankA : BOOL; // Manual Override Input for Tank A

PumpTimer : TON; // Timer structure for 2 minutes

END_VAR

// Initialize timer

PumpTimer(IN := FALSE, PT := T#2m); // 2 minutes timer

// Pump Control Logic

IF ManualOverrideTankA THEN

IF FloatSwitchTankB THEN

Pump := TRUE; // Activate pump only if Tank B switch is ON

PumpTimer(IN := TRUE); // Start timer

ELSE

Pump := FALSE; // Deactivate pump if Tank B switch is OFF

PumpTimer(IN := FALSE); // Stop timer

END_IF;

ELSE

Pump := FALSE; // Deactivate pump if override is not active

PumpTimer(IN := FALSE); // Stop timer

END_IF;

// Check Timer Done Status

IF PumpTimer.Q THEN

Pump := FALSE; // Stop pump when timer is done

END_IF;

END_PROGRAM

- Refer to the Connected Components Work Bench Manuals here to write a program to override float switch for Tank B but only run the pump for 2 minutes when Tank A switch is ON.

PROGRAM TankAControl

VAR

FloatSwitchTankA : BOOL;         // Input for Float Switch of Tank A

FloatSwitchTankB : BOOL;         // Input for Float Switch of Tank B

Pump : BOOL;                     // Output for Pump

ManualOverrideTankA : BOOL;      // Manual Override Input for Tank A

PumpTimer : TON;                 // Timer for 2 minutes

END_VAR

// Set the timer duration to 2 minutes

PumpTimer(IN := FALSE, PT := T#2m);

// Pump Control Logic

IF ManualOverrideTankA AND FloatSwitchTankB THEN

IF NOT PumpTimer.Q THEN

Pump := TRUE;                 // Activate pump

PumpTimer(IN := TRUE);        // Start the timer

END_IF;

ELSE

IF NOT PumpTimer.Q THEN

Pump := FALSE;                // Deactivate pump if conditions are not met

PumpTimer(IN := FALSE);       // Reset the timer

END_IF;

END_IF;

// Check Timer Done Status

IF PumpTimer.Q THEN

Pump := FALSE;                    // Stop pump when timer is done

PumpTimer(IN := FALSE);           // Reset the timer for future cycles

END_IF;

END_PROGRAM

- Refer to the Connected Components Work Bench Manuals here to write a program to run the pump only when both Tank A and Tank B float switches are ON.

PROGRAM TankABControl

VAR

FloatSwitchTankA : BOOL;      // Input for Float Switch of Tank A

FloatSwitchTankB : BOOL;      // Input for Float Switch of Tank B

Pump : BOOL;                  // Output for Pump

END_VAR

// Pump Control Logic

IF FloatSwitchTankA AND FloatSwitchTankB THEN

Pump := TRUE;                  // Activate pump if both float switches are ON

ELSE

Pump := FALSE;                 // Deactivate pump if either switch is OFF

END_IF;

END_PROGRAM

Upload your preparations on the drive before doing the lab.

# Practical Experiment

This will be posted later.

# Lab Report

1. Use these guidelines https://guides.libraries.indiana.edu/c.php?g=992698&p=7182653  to write your individual lab report detailing your answers for sections 1 to 4.